A STUDY ON THE RELIABILITY CONTROL METHOD FOR PREVENTING SURGE OF HIGH PRESSURE CENTRIFUGAL AIR-BLOWER

Hu Guoqing1 Li Yankun2 Li Weikun3 Pan Kelei2

1Department of Mechanical and Electrical Engineering

Xiamen(Amoy) University, Xiamen 361005, China

2Yunnan Tin Corpo.,Gejiu,Yunnan 661400

3Yunnan Kunming Iron and Steel Corp., Anning 650000

# ABSTRACT

This paper studies in detail the factors leading to the surge and the preventative surge control theory of the type of D200-0.28/0.97 high pressure centrifugal air-blower from the experience of installing, testing and using it in the nonferrous metal industries, a simple and reliable preventative surge control method is presented. The preventative surge control point is calculated in the centrifugal air-blower and the operation specification of preventative control surge is put forward. It can be proven that the preventative surge control method is simple, reliable, safe and particle.

1. INTRODUCTION

The type of D200-0.28/0.97 high centrifugal air-blower (DHAB) has been used as air-inlet equipment for the fuming furnace engineering series in Gejiu Tin Smelter, Yunnan Tin Corporation. Yunnan, China, because it is a key piece of equipment in the whole smelting process. The process of tin smelting depended directly on whether the DHAB is safe handled. The surge problem of the DHAB has been a common and main fault of the DHAB. In order to ensure that the machine is safe handled. It is necessary for us to understand the factors leading to the surge and how to take a good method to prevent it.

The technical requirement of air supplied by the high pressure air-blower in smelting process is as fellows:

medium:			air

air pressure		p=0.059~0.098MPa (gauge pressure)

air flow			Q=2.5~3m3s

the main characteristic of the D200-0.28/0.97 type of centrifugal air-blower is as fellows:

medium:			air

inlet flowrate		Qj=0.333m3s

inlet pressure		pj=0.095MPa(absolute pressure)

inlet temperature	tj=24oC

inlet specific weight	gj=1.079kgfm3

outlet pressure		pc=0.274MPa(absolute pressure)

power			N=535KW

revolution per minute		n=11629 (rpm)

adiabatic index			k=1.4

relative humidity		=78%

2. ANALYZE THE FACTORS CAUSING THE SURGE OF CENTRIFUGAL AIR-BLOWER

When two-phase flow (fluid and solid) was interacted and if the periodic vibration occurs, this phenomenon is called surge. The surge phenomenon of centrifugal air-blower is caused as follows:

2.1. Rotating separation.

When the inlet flow of the centrifugal air-blower reduce to some point, it will begin to separate in one or more blades, and therefore affect the direction of inlet air of the blades nearby; a change of the impulse blade angle of the inlet air will cause, Air in the separation region to move to the inverse direction of the blade rotation, then the moving relative velocity is smaller than that of the rotation of the blade. In the absolute moving, air in the separation regions will direct to rotation direction of the blade and the moving speed is also smaller than that of the rotation of the blade, these phenomena occur to all the blades at the same time, this is because:

(1) The process of installing and the sharp of the blade may not have a complete symmetry.

(2) Air is an anisotropy flow in the blade.

If air separation is occurred in a blade, the flow areas to the blade or those near to it will be reduced, airflow direction will be changed, and air separation of the next blade will be affected as well. It is just like that air separations move from the back of one blade to that of the next, which we call rotating separation. The rotating separation of the centrifugal air-blower is the prelude to occur the surge.

2.2. Surge.

When rotating separation takes place, the back pressure of the centrifugal air-blower is lower than that of the tube network, at the same time, causing air in the tube network system to begin a return flow which will make instantaneously up for the deficiency of the flow in the stage blade, then the system will recover its normal operation. If the return air is pressured to the normal direction, airflow in the blade will be reduced, the pressure will suddenly declined. Then air in the equipment will return to flow the blade, this phenomenon happens again and again, so it is called “surge." The surge always occurs when the flow of the system is low. At the beginning of the surge, the flow is in the smooth region of the pressure-flow curve of the centrifugal air-blower in fig.1. When the flow is lower than the beginning surge flow and pressure declines, the surge occurs. Figure 1 indicates the characteristic curve of the centrifugal air-lower at the constant rotation speed, which can be divided into two sections: surge limit, i.e. main flow section and obstacle (stagnation point), the basic slope section is caused in the case that the operation of the blade in normal and its pressure depends on air density, diameter of the blade and the rotation speed of the centrifugal air-blower, the shape of the characteristic curve depends on the blade angle, the speed of the outer edge of the blade and the relative speed of the air to the blade. The stagnation or obstacle function occurs when the flow is greater than that of the design point, and the flow exceeds the basic slope section of air compressor.

There are some pressure losses between the outer edge of the blade and the inlet edge of the next blade. The surge occurs when steady periodic air separation phenomenon is appeared. As the surge happens, it will produce a strong impulse wave at the edge of the centrifugal air-blower blade, which will make the blade vibrate, even bringing about a fatigue fracture, causing the whole set of equipment vibrate violently and generate a big noise, and at last the whole machine will paralyze, so the centrifugal air-blower is strictly prohibited from working at the state of the surge.

3. ANALYZING THE PREVENTATIVE SURGE CONTROL METHOD

3.1. Preventative surge control theory.

The characteristic curve of the centrifugal air-blower is presented in Fig.2. The upper left region is a surge region and the down right region is a normal operation region (i.e. stable region). The centrifugal air-blower works well at the right of the surge line. In figure 2., point “A” indicates that the centrifugal air-blower operates at the external region of the surge. However if the flow reduces, in the case of constant rotation speed, the point “A” will be moved to the left region of the surge line. Thus, the centrifugal air-blower will operate at the state of unstabilization, which the surge will take place. In order to eliminate the surge, the point of the centrifugal air-blower tube network system can be moved to the stabilized region or the surge boundary lines being moved to the lower flow region.

3.1.1. Change the tube network characteristic to realize the moving
of the operation point.

The characteristic curve of the centrifugal air-blower and the tube network can be represented as the pressure-flow curve in fig.3, the curve a, b, c represents of the resistance characteristic curve of the tube network system in case of a changing pressure, respectively. S represents the tube network resistance characteristic curve in case of a constant pressure. Ps represents constant pressure; QB represents surge control flow. When the centrifugal air-blower operates at the safe operation point “A”, as QA>QB.so,QA−QB=DQ>0, thus, the centrifugal air-blower operates at the steady operation region, When the tube network resistance increases, the tube network characteristic will move to point “C”, if the centrifugal air-blower works at the constant pressure, then, the outlet pressure will be constant, so the operation point of the centrifugal air-blower will move from point “C” to point “B”. In order to attain this objective, as the n=constant, it can: a) to change the tube network resistance, b) to throttle the flow rate of the outlet tube, so the centrifugal air-blower will move away from surge point to the steady operation region.

3.1.2. Changing the centrifugal air-blower inlet state parameters to realize the moving of the operation point.

When the rotation speed of the centrifugal air-blower is constant, if the displacement of throttle plate of the inlet throttle valve is changed, as the matter of fact, we are changing the status parameters of the centrifugal air-blower, with a corresponding change of the characteristic curve of the centrifugal air-blower. If the centrifugal air-blower operates at the operation point S, the operation parameters are pressure Ps and the flow rate is Qs, curve d is a characteristic curve of the open displacement of the inlet throttle valve and the curve b is the characteristic curve of the tube network. When the resistance of the tube network increases, the characteristic curve of the tube network will move from curve b to curve c, thus, the operation point is Sdand the working parameters are PsdandQsd, As Psd>Ps i.e. Psd−Ps=DP>0, thus, at this time, if it begins to close the inlet throttle valve, when the displacement of the inlet throttle valve reduces to some extent, the inlet state parameters of the centrifugal air-blower will be changed too, and making the characteristic curve a of the centrifugal air-blower moves to curve e, thus, it makes curve e intersects tube network characteristic curve c at the point Se. In the case of this condition, the operation parameters are changing to Psd andQsd, and make Psd=Ps, so Qse<Qs; On the contrary, the resistance of the tube network system decreases. In the same way, if the displacement of the inlet throttle valve opens to some extent. We can make the centrifugal air-blower work at the operation point Sf, the operation parameters are changing to Psd and Qsd, and Qse>Qs. Therefore, if we want to change the inlet parameters of the centrifugal air-blower, we can adopt: a) to change the rotation speed n of the centrifugal air-blower. b) to rotate the operating blade or pilot flow blade at the constant rotating speed n: c) to throttle the displacement of the inlet orifice at the constant rotating speed n (see Fig.4). Using those three methods can change the flow rate of the centrifugal air-blower, from which the outlet pressure of the centrifugal air-blower will be kept constant, escaping the surge point Sd. Therefore, it meets the requirement of the technological process that the out-put pressure of the centrifugal air-blower should be stable.

3.2. Preventative surge control method.

After having done a theoretical analysis of the surge control theory, we come to a preventative surge method is as fellows:

1) Bypass

In order to make the flow in the blade of the centrifugal air-blower greater than that of the surge point. We can use the bypass value to make air return to the inlet orifice.

2) Exhaust

Exhaust some air at the outlet orifice of the centrifugal air-blower, and the systems will stabilize, however, it is impossible to do that except air.

3) Adopt throttle.

Throttle the inlet pilot blade of the centrifugal air-blower and the operation will move point into the right of characteristic curve.

4) Rotating throttle

Decrease the rotating speed and the surge flow will be moved into the left section, so and therefore the stability operation region is expended. However, it is impossible that the pressure and the flow rate are kept constant simultaneously.

5) Dual-valve throttle

Dual valves are installed at the outlet tube system of the centrifugal air-blower. The volume is constant between them. We can adjust the throttle valve of the centrifugal air-blower to make the surge amplitude decline.

6) Constant flow throttle

If we adopt the exhaust throttle method to change the characteristic curve of the centrifugal air-blower and maintain the constant inlet flow, we can be sure that the centrifugal air-blower will work at the stability regions.

7) Constant pressure throttle

If we adopt the inlet throttle method to change the characteristic curve of the centrifugal air-blower and maintain the constant outlet pressure we can be sure that the centrifugal air-blower will work at the stability regions.

8) Preventative surge safes protect throttle

If we adapt the method of exhaust tube drop out (or air return to the inlet tube) to change the characteristic curve of the tube network, we can be sure that the surge problem (or unstability regions) will be avoided.

4. THE APPLICATION OF THE PREVENTATIVE SURGE CONTROL METHOD

4.1. The design of the preventative surge control method.

The design of the type of D200-0.28/0.97 centrifugal air-blower is to adopt preventative surge control system in fig.5. The machine is not only safe and reliable, but also economical and practical. The exhaust valve is full open and valve 5, 6 are completely closed when the centrifugal air-blower works under the normal condition. While the centrifugal air-blower moves near to the surge point, the exhaust valve 5 will be completely open. (When the exhaust valve 5 acts up thus close valve 4 and open manual throttle valve 6). At the same time, we can exhaust some air in the outlet tube system of the centrifugal air-blower or open increasingly the manual valve 2, and increase the inlet air flow to change the characteristic of tube network system of the centrifugal air-blower and prevent the centrifugal air-blower from working at the surge state.

4.2. Determine and calculate the setting value of the preventative surge control point.

Based on the experiment report on the performance of the centrifugal air-blower and data conversion table 1, the characteristic curve of the centrifugal air-blower is drawn as fig.6.

Table 1.

Experiment report on the performance of D200-0.28/0.97 type and data conversion table of the centrifugal air-blower.

| Volume flower (m3s) | 3.771 | 3.499 | 2.938 | 2.568 | 2.331 | 1.944 |
| --- | --- | --- | --- | --- | --- | --- |
| Outlet pressure (MPa) | 0.197 | 0.246 | 0.281 | 0.286 | 0.289 | 0.288 |

4.2.1. Determine the flow of the surge control point.

In term of the characteristic curve and conversion table, the minimum inlet flow is Qjimn=1.933m3/s  (i.e., surge point flow) In order to be safe, the flow of the surge control point is usually greater than eight percent of the surge flow, thus:

Qjimnc=1.933(1+8%)=2.088m3/s							(1)

so, the flow of the surge control point is 2.088m3/s

4.2.2. Determine the pressure of the surge control point.

The local atmospheric pressure is P=645mmHg conversion,

645735.6kgfcm2=0.877kgfcm2=0.0859MPa					(2)

Inlet negative pressure is Pjf=23.5mmHg, so the inlet pressure is:

645−23.5735.6kgfcm2=0.845kgfcm2=0.0828MPa				(3)

From the performance experiment report and conversion number, when the inlet minimum is Qjmin=1.933m3/s, the outlet pressure is Pcmax=0.288MPa (absolute pressure)

So the pressure of the surge point of the centrifugal air-blower is equal to the highest outlet pressure minus local atmospheric pressure, thus:

Pcmax=0.2880.095´0.0828−0.0859=0.165MPa (gauge pressure)			(4)

In order to be safe, the pressure of the surge control point is usually smaller than 8%~10% of that surge point, here is 8.5%, thus:

Pcmaxc=0.165(1−8.5%)=0.15MPa (gauge pressure)				(5)

So the pressure of the surge control point is 0.15MPa. When the outlet pressure of the centrifugal air-blower is increased to 0.15MPa or the inlet flow of the centrifugal air-blower is decreased to 2.083m3/s. The centrifugal air-blower equipment will send out sound and light emergency alarm messages, and it will automatically open bypass valve at the exhaust tube system, decreasing the outlet back-pressure of the equipment, and increasing the inlet volume flow, so the work point will be moved to large flow region. When the outlet pressure of the centrifugal air-blower tube system decreases to the lower of the 0.15MPa, the bypass valve of the exhaust tube system will automatically close; the centrifugal air-blower will recover to normal operating state.

4.3. The hand requirement of the preventative surge control.

Not only should measures be taken to prevent the surge when designing, but also should the field workers be instructed how to determine the surge key point and how to take corresponding action when the surge happens.

4.3.1. Determine the key point of the surge.

(1) Audit the noise sent out by exhaust tube system, if it is like the asthma patient breathing, and at the same time, if the periodic rumble is produced, the surge will occur.

(2) Observe the change outlet pressure gauge and the inlet flow meter of the centrifugal air-blower tube system; if the valve distribution is very great, the surge will occur.

(3) Observe the vibration of the main body and bearing of the centrifugal air-blower, if the machinery vibrates violently, and the amplitude of the machinery and bearing increase remarkably, the surge will take place.

4.3.2 To take emergency action when the surge occurs.

(1) Open the exhaust check valve 6 in the bypass tube system as far as quickly to decrease the outlet pressure of the machinery, when the surge occurs.

(2) Stop operating the machinery immediately when the above-mentioned measures are ineffective.

5. CONCLUSION

This simple and reliable preventative control method for high centrifugal air-blower has been successfully applied about in the fuming furnace engineering series in Gejiu Smelting works, Yunnan Tin Corporation for about seven years. By using it the surge has never happened, so it can be proven that it is a successful method for preventing surge. Not only has it solved the problem existing in technological process, but also is it economic, reliable, simple and practical method to uses. Especially, when used to solve the preventative surge problem of a small type of high-pressure centrifugal air-blower. The conclusion also fits other nonferrous metal smelting process, owing to its great market value, the vista of its application will be.

REFERENCES

1. The theory and calculation of axis and centrifugal air compressor. China metallurgical industry press, 1964, N1.

2. Li YanKun. Analyze preventative surge factors and preventative measure for the high-pressure centrifugal air-blower, nonferrous metallurgy, 1994, vol.6.

Поступила в редакцию 4 февраля 2000 года.